## Coega Kop Telemetry Panel
Spectrum Addresses
MW# | BIT # | DATA |  |  |  | Scaling | Comments
Common
100 |  | COMMON BOOLEAN WORD | PLC | to | Telemetry
100 | 0 | PLC Communication Bit
100 | 1 | Actuator Opened Position
100 | 2 | Actuator Closed Position
100 | 3 | Actuator Fault
100 | 4 | Manual Mode
100 | 5 | Auto Mode
100 | 6 | Remote Control Mode
100 | 7 | PR Level Probe Fault
100 | 8 | Warning Reservoir Level
100 | 9 | Spare
100 | 10 | Spare
100 | 11 | Spare
100 | 12 | Spare
100 | 13 | Spare
100 | 14 | Spare
100 | 15 | Spare
101 |  | Reservoir Level | PLC | to | Telemetry | 0-100 | % INT
Control
102 |  | CONTROL BOOLEAN WORD | Telemetry | to | PLC
102 | 0 | PLC Communication Bit
102 | 1 | Actuator Open
102 | 2 | Actuator Close
102 | 3 | Spare
102 | 4 | Spare
102 | 5 | Spare
102 | 6 | Spare
102 | 7 | Spare
102 | 8 | Spare
102 | 9 | Spare
102 | 10 | Spare
102 | 11 | Spare
102 | 12 | Spare
102 | 13 | Spare
102 | 14 | Spare
102 | 15 | Spare
MAC Automation Addresses
MW# | BIT # | DATA |  |  |  | Range | Scaling Factor | Unit | Data Type | Comments
Common
200 |  | COMMON BOOLEAN WORD | PLC | to | Telemetry
200 | 0 | Charger OK
200 | 1 | Actuator Opening
200 | 2 | Actuator Opened Position
200 | 3 | Actuator Closing
200 | 4 | Actuator Closed Position
200 | 5 | Actuator Fault
200 | 6 | Manual Mode
200 | 7 | Auto Mode
200 | 8 | Remote Control Mode
200 | 9 | Control Valve 1
200 | 10 | Control Valve 2
200 | 11 | Warning Reservoir Level
200 | 12 | Level Signal Error
200 | 13 | Valve Chamber Pressure Error
200 | 14 | Grassridge Flow Rate Error
200 | 15 | Coega IDZ Flow Rate Error
201 |  | COMMON BOOLEAN WORD | PLC | to | Telemetry
201 | 0 | Motherwell North Flow Rate Error
201 | 1 | Spare
201 | 2 | Spare
201 | 3 | Spare
201 | 4 | Spare
201 | 5 | Spare
201 | 6 | Spare
201 | 7 | Spare
201 | 8 | Spare
201 | 9 | Spare
201 | 10 | Spare
201 | 11 | Spare
201 | 12 | Spare
201 | 13 | Spare
201 | 14 | Spare
201 | 15 | Spare
202 |  | Reservoir Level | PLC | to | Telemetry | 0-32767 | 1/1 | % | INT
203 |  | Valve Chamber Pressure | PLC | to | Telemetry | 0 - 32767 | 1000/1 | bar | INT
204 |  | Grassridge Flow Rate | PLC | to | Telemetry | 0 - 32767 | 10/1 | Ml/d | INT
205 |  | Grassridge Total Flow | PLC | to | Telemetry | 0 - 2147483647 | 1/1 | Ml | DINT
206
207
208 |  | Coega IDZ Flow Rate | PLC | to | Telemetry | 0 - 32767 | 10/1 | Ml/d | INT
209 |  | Coega IDZ Total Flow | PLC | to | Telemetry | 0 - 2147483647 | 1/1 | Ml | DINT
210
211
212 |  | Motherwell Flow Rate | PLC | to | Telemetry | 0 - 32767 | 10/1 | Ml/d | INT
213 |  | Motherwell Total Flow | PLC | to | Telemetry | 0 - 2147483647 | 1/1 | Ml | DINT
214
215
216
Control
250 |  | CONTROL BOOLEAN WORD | Telemetry | to | PLC
250 | 0 | Control Valve 1 Open/Close
250 | 1 | Control Valve 2 Open/Close
250 | 2 | Actuator Open
250 | 3 | Actuator Close
250 | 4 | Spare
250 | 5 | Spare
250 | 6 | Spare
250 | 7 | Spare
250 | 8 | Spare
250 | 9 | Spare
250 | 10 | Spare
250 | 11 | Spare
250 | 12 | Spare
250 | 13 | Spare
250 | 14 | Spare
250 | 15 | Spare

## Coega Kop Remote IO Panel
MW# | BIT # | DATA |  |  |  | Range | Scaling Factor | Unit | Data Type | Comments
Common
200 |  | COMMON BOOLEAN WORD | PLC | to | Telemetry
200 | 0 | Coega IDZ Flow Rate Error
200 | 1 | Motherwell North Flow Rate Error
200 | 2 | Spare
200 | 3 | Spare
200 | 4 | Spare
200 | 5 | Spare
200 | 6 | Spare
200 | 7 | Spare
200 | 8 | Spare
200 | 9 | Spare
200 | 10 | Spare
200 | 11 | Spare
200 | 12 | Spare
200 | 13 | Spare
200 | 14 | Spare
200 | 15 | Spare
201 |  | COMMON BOOLEAN WORD | PLC | to | Telemetry
201 | 0 | Spare
201 | 1 | Spare
201 | 2 | Spare
201 | 3 | Spare
201 | 4 | Spare
201 | 5 | Spare
201 | 6 | Spare
201 | 7 | Spare
201 | 8 | Spare
201 | 9 | Spare
201 | 10 | Spare
201 | 11 | Spare
201 | 12 | Spare
201 | 13 | Spare
201 | 14 | Spare
201 | 15 | Spare
202 |  | Coega IDZ Flow Rate | PLC | to | Telemetry | 0 - 32767 | 10/1 | Ml/d | INT
203 |  | Coega IDZ Total Flow | PLC | to | Telemetry | 0 - 2147483647 | 1/1 | Ml | DINT
204
205
206 |  | Motherwell Flow Rate | PLC | to | Telemetry | 0 - 32767 | 10/1 | Ml/d | INT
207 |  | Motherwell Total Flow | PLC | to | Telemetry | 0 - 2147483647 | 1/1 | Ml | DINT
208
209
210